### PART 1 - GENERAL

- DESCRIPTION

  - Work included:

    - Hot-rolled steel double weatherstripped windows with fixed, project-in, project-out configurations.

    - All window anchors, mullions, covers and trim.

    - Stainless steel insect screens for all operating ventilators (optional).

    - Factory applied Hope’s Power of 5 finishing system.

  - Related work specified elsewhere:

    - Glass, glazing and glazing materials, Section 08810.

    - Perimeter caulking, Section 07915.

    - Miscellaneous structural items, Section 05100.

- QUALITY ASSURANCE

  - Manufacturer shall have not less than 5 years experience in the fabrication of heavy custom steel windows and be a member of The Steel Window Institute (SWI).

  - Installation of windows shall be done by experienced window installers.

  - Allowable tolerances: Size dimensions + 1/16 inch.

  - Source quality control:

    - Air infiltration test:

      - Meets or exceeds ASTM E283.

      - Maximum air infiltration 0.50 CFM/Ft. of crack length with differential pressure across window unit of 6.24 PSF.

    - Water penetration test:

      - Meets or exceeds ASTM E331.

      - No water penetration for 15 minutes when window is subjected to a rate of flow of 5 gal./hr./sq. ft. with differential pressure across window unit of 4.50 PSF.

    - Field test:

      - Field testing criteria (when applicable) shall be in accordance with AAMA 502.

    - Structural test:

      - Meets or exceeds ASTM E330.

      - No damage at 60 psf.

    - Forced entry test:

      - Meets or exceeds ASTM F588.

      - Grade 40 @ 300 pounds.

    - Impact test:

      - ASTM E1996.

      - Missile level D, wind zone 4.

    - Cyclic load test:

      - ASTM E 1886.

      - Positive and negative cyclic testing to 50 psf.

    - Hope’s Power of 5 finishing process shall meet or exceed the following designations:

      - Acid Pickling SSCP-SP8.

      - Hot Dip Galvanize ASTM A123.

      - Adhesion: ASTM D 3359, no loss.

      - Hardness: ASTM D 3363 (pencil), H min.

      - Salt Spray: ASTM B 117, passes 3000 hrs.

      - Humidity: ASTM D 2247, 3000 hours, few #8 blisters.

      - Impact Resistance (3mm): ASTM D 2794, no loss.

      - Color Retention: ASTM D 2244, 5 year less than or equal to 5 delta E.

      - Chalk Resistance: ASTM D 4214, #8 rating.

      - Gloss Retention: ASTM D 523, greater than or equal to 30 percent retention.

    - Upon request, the window manufacturer shall provide a test report from a qualified independent U.S. testing laboratory regularly engaged in testing windows to verify that products conform to these test requirements.

- SUBMITTALS

  - Samples (as requested by architect):

    - Typical corner sample of specified window profile with glazing beads.

    - Sample of specified muntin (6″ long), showing welded intersections and glazing beads.

    - Color sample of finish.

    - Hardware.

  - Shop drawings and manufacturer's literature:

    - Submit for approval shop drawings showing window and installation details, including anchorage, fastening and recommended sealing methods.

    - Dimensioned elevations showing window opening and window sizes.

    - The manufacturer shall not commence any work until shop drawings have been approved.

    - Color charts for finishes.

- PRODUCT, STORAGE AND HANDLING

  - The General Contractor shall be responsible for the protection and storage of the windows after delivery to the site.

  - Store in designated areas in an upright position on wood slats or on a dry floor in a manner that will prevent damage.  Ventilate canvas or plastic coverings to prevent humidity buildup.

- WARRANTY

  - Provide Hope’s 10 year Limited Warranty.

PART 2 - PRODUCT AND FABRICATION

- Manufacturers:

  - Furnish all labor and materials to complete the fabrication of windows as shown on architect’s drawings and as specified herein. All windows covered by this specification shall be domestically manufactured in the U.S.A.

  - Manufacturers: Subject to compliance with requirements covered in this specification, provide products by Hope’s Windows, Inc. – Jamestown, NY (phone: 716-665-5124, e-mail; sales@hopeswindows.com) whose name and products are used to establish the standard of workmanship.

  - Substitutions: Written approval necessary 10 days prior to bid through submission of the following:

    - Full-size window/door samples matching required scope.

    - Applicable test reports as outlined in Quality Assurance Section 1.2.

    - List of five recently completed projects of similar size and scope.

- Materials:

  - Heavy custom double weatherstripped windows shall be manufactured from solid hot-rolled steel shapes.

    - Profiles made from steel with flanges rolled integrally at the mill.

    - Perimeter frames and ventilator sections shall have glazing rebates providing an unobstructed glazing surface of at least 3/8".

    - The exterior side of the glazing rebate shall have a coved recess integrally rolled in the profile.  Applied tapered adapters will not be acceptable.

    - Combined weight of frame and ventilator profiles shall be a minimum of 4.68 pounds per lineal foot. Frame profile alone shall not weigh less than 1.85 pounds per lineal foot.

    - All steel profiles to be a minimum of 1-7/8ʺ in depth.

    - The frame profiles shall have integral grooves located on the interior bedding contacts for the reception of weatherstripping.

  - Muntins:

    - True divided lite muntins:

      - Hot-rolled steel muntins shall have a 7/8” sightline with integral coves to match perimeter frame and ventilator profiles.

  - Glazing beads shall be extruded aluminum Alloy 6063-T5 with a minimum thickness of .045 inches.

  - Weatherstripping shall be extruded EPDM closed cell sponge, closed cell neoprene, or flexible silicone, or polyethylene clad urethane foam.

  - Operable Hardware (Select from the following):

    - Project-Out Ventilators:

      - Fastener: Brass or bronze cam fastener.

      - Ventilators shall be hung on heavy-duty stainless steel four bar hinges with brass friction shoes.

    - Project-In Ventilators:

      - Fastener: Brass or bronze cam fastener; or bronze spring catch for ventilators beyond reach.

      - Ventilators shall be hung on heavy-duty stainless steel four bar hinges with brass friction shoes.

  - All screws that are furnished by Hope’s, for hardware, trim, covers, anchoring, weather bars, water dams, screens, etc. shall be non-ferrous brass or stainless steel.  Glazing bead retainer screws are plated steel.

  - Stainless Steel Insect Screens (Optional):

    - Frames shall be roll-formed 20 gauge stainless steel.

    - Stainless steel screens shall be .011 diameter wire, woven to 14 x 18 mesh count.  Mesh is available in several types of material; see screen section for type of mesh (specify) and further screen specifications.

  - Power of 5 Finishing:

    - Cleaning.

    - Pretreatment.

    - Brush-Off Blast Cleaning.

    - Epoxy Powder Primer.

    - Polyester Powder Top Coat.

- FABRICATION

  - Fabricate steel windows in accordance with approved shop drawings.

  - Corners of frame and ventilator shall be mitered or coped then solidly welded.  Exposed and contact surfaces shall be finished smooth flush with the adjacent surfaces.  All interior and exterior rail bar and muntin joints shall be welded and ground smooth.

  - Muntins:

    - True divided lite muntins shall be welded to the perimeter frame.  Muntin intersections shall be slotted, cross notched and welded.

  - Glazing:

    - All windows shall be designed for inside glazing.

    - Provide replaceable continuous snap-in glazing beads to suit the glass as specified.

    - Glazing beads shall be cut and shop fitted to each glass lite prior to shipment.

  - Weatherstrip:

    - All ventilators shall receive continuous EPDM weatherstripping that shall be applied to the integral weatherstrip grooves on the interior. Exterior shall have adhesive backed silicone bulb EPS on sealing leg contact surfaces between the frame and ventilator sections.

  - Operable Hardware (Select from the following):

    - Project-Out ventilators:

      - Ventilators shall be hung on heavy-duty stainless steel four bar hinges, having friction maintained by a sliding brass shoe with screw adjustment.

      - Provide two fasteners per ventilator where sash width exceeds 48".

    - Project-In ventilators:

      - Ventilators shall be hung on heavy-duty stainless steel four bar hinges, having friction maintained by a sliding brass shoe with screw adjustment.

      - Provide two fasteners per ventilator where sash width exceeds 48".

  - Stainless Steel Insect Screens (Optional):

    - Stainless steel screen frames shall be finished to match the windows.

    - Stainless steel screens shall be rewireable to allow for mesh replacement.

    - Stainless steel screen fastenings shall permit easy attachment and removal from the interior.  See screen section for further specifications.

- FACTORY FINISHING

  - Cleaning:

All hot-rolled steel profiles must be acid pickled to white metal as defined by SSPC – SP8 creating a pristine, white metal substrate which is paramount to achieving ultimate finish performance.

  - Pretreatment:

Following welding and all machining operations, hot-rolled products and accessories are subjected to the following pretreatment process.

    - Hot-Dip Galvanize.

      - Parts are cleaned and immersed in a molten pool of pure zinc per ASTM A123 to create a thickness of 4 - 8 mils of cathodic protection.

    - Quality Control.

    - Mechanical Cleaning.

  - Brush-Off Blast Cleaning:

    - Galvanized parts shall be brush-off blast cleaned in accordance with SSPS-SP16 to profile surface prior to primer application.

    - All Parts shall be oven heated prior to finishing to prevent outgassing through epoxy primer.

  - Epoxy Powder Primer:

Following pretreatment and brush-off blast cleaning all parts shall receive an abrasion resistant epoxy powder coat to ensure ultimate substrate protection. Epoxy powder primer is intended as an intermediate finish applied prior to the final finish top coat.

    - Within 12 hours of hot-dip galvanizing pretreatment all frames and accessories shall receive an epoxy powder primer for abrasion resistance.

    - After hot-dip galvanizing has been cleaned, brush-off blasted, and oven outgassed – epoxy powder primer is applied electrostatically to a dry film thickness (DFT) of 2.0-4.0 mils.

    - Parts are oven baked in preparation of top coat application.

  - Polyester Powder Top Coat:

The top coat defines the final stage to the overall aesthetics and performance of the finished product.

- Polyester powder top coat shall be applied immediately over epoxy powder primer.

- Powder top coat is electrostatically applied to a dry film thickness (DFT) of 2.0 – 4.0 mils.

- Parts are oven baked to fully cure.

  - Power of 5 Overview:

    - Combined overall dry film thickness (DFT) of hot-dip galvanizing, epoxy primer, and polyester powder top coat shall be between 8.0 – 16.0 mils.

    - Overall process shall provide full documented compliance with the following criteria:

      - SSCP-SP8 for Acid Pickling

      - ASTM A123 for Hot Dip Galvanize

      - Adhesion: ASTM D 3359, no loss.

      - Hardness: ASTM D 3363 (pencil), H min.

      - Salt Spray: ASTM B 117, passes 3000 hrs.

      - Humidity: ASTM D 2247, 3000 hours, few #8 blisters.

      - Impact Resistance (3mm): ASTM D 2794, no loss.

      - Color Retention: ASTM D 2244, 5 year less than or equal to 5 delta E.

      - Chalk Resistance: ASTM D 4214, #8 rating.

      - Gloss Retention: ASTM D 523, greater than or equal to 30 percent retention.

PART 3 - EXECUTION

- INSPECTION

  - Window openings shall conform to details, dimensions and tolerances shown on the window manufacturers approved shop drawings.

  - Conditions which may adversely affect the window installation must be corrected before installation commences.

  - The wash down of the adjacent masonry must be completed before erection commences to prevent damage to the finish by the cleaning materials.

- INSTALLATION

  - Windows specified under this section shall be installed by experienced personnel.

  - Install windows in openings in strict accordance with approved shop drawings.

    - Set units plumb, level and true to line, without warp or rack of frames.

    - Anchor units securely to surrounding construction with approved fasteners.

    - The exterior joints between the windows, trim and mullions shall be properly sealed water-tight with an approved sealant and neatly pointed.

  - Attach ventilator hardware, as required, and adjust ventilators to operate smoothly free from twist and to be weather-tight when closed.

  - Attach loose muntin grids per approved shop drawings, if applicable.

  - Repair any abraded areas of the factory finish.

- CLEANING

  - Window installer shall leave window surfaces clean after installation and ready to receive glass and glazing.  The window installer will not be responsible for final cleaning.